## Slide 1: Unsymmetrical fault

## Slide 2: Single Line-to-Ground Fault
A single line-to-ground fault on a transmission line occurs when one conductor drops to the ground or comes in contact with the neutral conductor.

## Slide 3
Circuit diagram of single line-to-ground fault
Most frequently occurring fault.
Usually assumed the fault on phase – a for analysis purpose. The phase a is connected to ground at the fault point F as shown in a figure below, phase – b and phase c are healthy. Ia, Ib and Ic are the current and Va, Vb and Vc are the voltage across the three phase line a, b and c respectively. The fault impedance of the line is Zf.
Since only phase a is connected to ground at the fault, phase b and c are open circuited and carries no current; So, fault current is Ia
Also, Ib = 0,
  Ic = 0.
  The voltage at the fault point F, Va = Zf Ia.

## Slide 4
The symmetrical components of the fault currents are
Substuting, we get
or, =
Therefore, Ia0 = Ia1 = Ia2 =
or, Ia = 3 Ia0 = 3Ia1 = 3Ia2
From the above expressions of positive, negative and zero sequence components of current in faulted phase A, we observe that all the sequence currents are equal in magnitude and phase.
The voltage at the fault point F, Va = Zf Ia
Vao + Va1 + Va2 = (Iao + Ia1 + Ia2) Zf =3 Zf Ia1
S0, Sum of sequence voltages equals 3Zf Ia1.
Or, E1-Ia1Z1 – Ia2Z2 - Ia0 Z0 = 3Ia1 Zf

## Slide 5
Or, E1 - Ia1 (Z1 + Z2 +Z0 ) = 3Ia1 Zf
Therefore, Ia1 = 2 = Ia0
Hence, +ve, −ve and zero sequence networks are connected in series.
And, If = Ia = (Ia1 + Ia2 + Ia0) = 3 1 =